## Sheet 1
PIPE HEADLOSS & POWER CALCULATOR
Key Data | Values to be entered shown in blue
Flow | Ml/d | 352.695 | WW 2007-08 Average
| m3/s | 4.0821
| l/s | 4082.1181
Diameter | mm | 3000 | 3.0m dia pipe
Length | m | 482803.2 | 300 miles
Pipeline Headloss Calculator - Using Colebrook White Equation
Pipeline Rougness Ks (mm) | mm | 0.15 | Cast Iron | (see Roughness Sheet)
f (Calculated) Darcy's Coeff |  | 0.0026361
Velocity m/s | m/s | 0.5775
Headloss (m) | m | 28.8453
Headloss (m/km) | m/km | 0.059746
Power Calculator using equation Power = 9.81 * Q * H / Efficiency
Static Lift | m | 100 | 100m
Total lift | m | 128.8453
Pump and Motor Efficiency | % | 70%
Power | kW | 7370.979
Operating hours/day | hrs | 24
Operating days/year | days | 365
Power Consumption | kWhrs/day | 176903.4955
| kWhrs/year | 64569775.855
Cost of power assumed | £/kW-hr | 0.095 | 9.5p/kWh
Operating cost | £/year | 6134128.7062
Operating cost | £/Ml | 47.6498

## Roughness
Pipe Material / Condition | Roughness (k (mm))
Drawn brass, copper | 0.0025
Glass, Perspex, fibreglass | 0.0025
New smooth steel pipe | 0.025
Cast iron | 0.15
Light rust | 0.25
Water mains with tuberculations | 1.2
Mature foul sewer | 3
Pre-cast concrete | 0.25
Corrugated plastic | 3.5